## Residual Fuel Oil #6
Table 1
TANK EMISSION CALCULATION FORM1
( Note - Cells in pink are input cells. All other cells are calculated cells. )
DIRECTIONS: |  | Fill in pink input cells with specific tank description, dimensions, throughput and paint absorptance factor. For paint absorptance factor included in Table 1a below.
Tank No. |  | T-501 |  | Tank type | Vertical fixed roof |  |  | Date |  | 2026-07-29 19:12
Material stored |  | Residual Fuel Oil No. 6 |  | Company |  |  |  | Performed by |  | Jimmy Peress
City |  | Newark |  | State | NJ
Description |  | Outdoor storage tank
|  | INPUT DATA | [5 empty] | CALCULATIONS
|  |  | Symbol |  | Units |  |  |  | Symbol |  | Units
Breathing losses
Molecular Weight | [6 empty] | Tank vapor space volume |  | Vv | 6217.75 | ft3
| Molecular weight |  | Mv | 190 | Lb/lb-mole |  | Vapor density |  | Wv | 1.9293e-06 | lb/ft3
Tank design data | [6 empty] | Vapor space expansion factor |  | KE | 0.064673
| Shell height |  | Hs | 40 |  |  | Vented vapor saturation factor |  | Ks | 0.99994 | ft2
| Diameter |  | D | 20 | ft
| Liquid height |  | Hl | 40 | ft | Breathing losses |  |  | LB | 0.28315 | lb/yr
| Avg. Liquid height |  | Hl | 20 | ft
| vapor space outage |  | Hvo | 20.2083 | ft | Working losses |  |  | Lw | 0.24239 | lb/yr
| Tank volume |  |  | 94002.9552 | gallons
| Turnovers |  | N | 10 |  | TOTAL LOSSES |  |  | LT | 0.52555 | lb/yr
| Net throughput |  | Q | 940032.91 | gallons/yr
| Tunover factor |  | KN | 1
| Working loss product factor |  | Kp | 1
Meteorological data | [7 empty] | Table 1a
| Daily ave. ambient temp. |  | TAA | 54.7458 | °F |  |  | Tank Paint Solar Absorptance
| Daily max. ambient temp. |  | TAX | 63.3833 | °F
| Daily min. ambient temp. |  | TAN | 46.1083 | °F |  |  | Tank Paint | Solar Absorptance
| Daily ambient temp. range |  | DTA | 17.275 | °F
| Tank paint solar absorptance (see adjacent table) |  | a | 0.68 |  |  |  | white/white |  | 0.17
| Daily total insolation factor |  | I | 1235.5816 | Btu/ft2-day |  |  | Aluminum/Specular |  | 0.39
[8 empty] | gray/light |  | 0.54
| Liquid bulk temperature |  | TB | 57.8258 | °F |  |  | Aluminum/Diffuse |  | 0.6
| Daily vapor temp. range |  | DTv | 35.9635 | °F |  |  | grey/medium |  | 0.68
| Daily ave. liquid surface temp. |  | TLA | 63.1081 | °F
| Daily max. liquid surface temp. |  | TLX | 72.099 | °F
| Daily min. liquid surface temp. |  | TlN | 54.1173 | °F
| VP @ daily ave. liquid surf. temp. |  | PvA | 0.0029477 | mm Hg
| VP @ daily max. liquid surf. temp. |  | PvX | 0.0051715 | mm Hg
| VP @ daily min. liquid surf. temp. |  | PvN | 0.00072401 | mm Hg
| Daily vapor pressure range |  | DPv | 0.0044475 | mm Hg
| Breather vent pressure setting range |  | DPB | 0.06 | psia
| Breather vent pressure setting range |  | DPB | 3.1029 | mm Hg
1Calculations performed on this spreadsheet are taken from the USEPA AP-42- Section 7.1 Organic Liquid Storage Tanks - January 1996. This spreadsheet is derived from materials provided by Jimmy Peress, PE, Tritech Consulting Engineers, 85-93 Chevy Chase Street, Jamaica, NY 11432 USA, Tel - 718-454-3920, Fax - 718-454-6330, e-mail - PeressJ@nyc.rr.com.

## Distillate Fuel Oil #2 & Diesel
Table 1
TANK EMISSION CALCULATION FORM1
( Note - Cells in pink are input cells. All other cells are calculated cells. )
DIRECTIONS: |  | Fill in pink input cells with specific tank description, dimensions, throughput and paint absorptance factor. For paint absorptance factor included in Table 1a below.
Tank No. |  | T-501 |  | Tank type | Vertical fixed roof |  |  | Date |  | 2026-07-29 19:12
Material stored |  | Distilllate Fuel Oil NO. 2 |  | Company |  |  |  | Performed by |  | Jimmy Peress
City |  | Newark |  | State | NJ
Description |  | Outdoor storage tank
|  | INPUT DATA | [5 empty] | CALCULATIONS
|  |  | Symbol |  | Units |  |  |  | Symbol |  | Units
Breathing losses
Molecular Weight | [6 empty] | Tank vapor space volume |  | Vv | 6217.75 | ft3
| Molecular weight |  | Mv | 130 | Lb/lb-mole |  | Vapor density |  | Wv | 0.00016674 | lb/ft3
Tank design data | [6 empty] | Vapor space expansion factor |  | KE | 0.064958
| Shell height |  | Hs | 40 |  |  | Vented vapor saturation factor |  | Ks | 0.9925 | ft2
| Diameter |  | D | 20 | ft
| Liquid height |  | Hl | 40 | ft | Breathing losses |  |  | LB | 24.3968 | lb/yr
| Avg. Liquid height |  | Hl | 20 | ft
| vapor space outage |  | Hvo | 20.2083 | ft | Working losses |  |  | Lw | 20.9493 | lb/yr
| Tank volume |  |  | 94002.9552 | gallons
| Turnovers |  | N | 10 |  | TOTAL LOSSES |  |  | LT | 45.3461 | lb/yr
| Net throughput |  | Q | 940032.91 | gallons/yr
| Tunover factor |  | KN | 1
| Working loss product factor |  | Kp | 1
Meteorological data | [7 empty] | Table 1a
| Daily ave. ambient temp. |  | TAA | 54.7458 | °F |  |  | Tank Paint Solar Absorptance
| Daily max. ambient temp. |  | TAX | 63.3833 | °F
| Daily min. ambient temp. |  | TAN | 46.1083 | °F |  |  | Tank Paint | Solar Absorptance
| Daily ambient temp. range |  | DTA | 17.275 | °F
| Tank paint solar absorptance (see adjacent table) |  | a | 0.68 |  |  |  | white/white |  | 0.17
| Daily total insolation factor |  | I | 1235.5816 | Btu/ft2-day |  |  | Aluminum/Specular |  | 0.39
[8 empty] | gray/light |  | 0.54
| Liquid bulk temperature |  | TB | 57.8258 | °F |  |  | Aluminum/Diffuse |  | 0.6
| Daily vapor temp. range |  | DTv | 35.9635 | °F |  |  | grey/medium |  | 0.68
| Daily ave. liquid surface temp. |  | TLA | 63.1081 | °F
| Daily max. liquid surface temp. |  | TLX | 72.099 | °F
| Daily min. liquid surface temp. |  | TlN | 54.1173 | °F
| VP @ daily ave. liquid surf. temp. |  | PvA | 0.37235 | mm Hg
| VP @ daily max. liquid surf. temp. |  | PvX | 0.49646 | mm Hg
| VP @ daily min. liquid surf. temp. |  | PvN | 0.27409 | mm Hg
| Daily vapor pressure range |  | DPv | 0.22237 | mm Hg
| Breather vent pressure setting range |  | DPB | 0.06 | psia
| Breather vent pressure setting range |  | DPB | 3.1029 | mm Hg
1Calculations performed on this spreadsheet are taken from the USEPA AP-42- Section 7.1 Organic Liquid Storage Tanks - January 1996. This spreadsheet is derived from materials provided by Jimmy Peress, PE, Tritech Consulting Engineers, 85-93 Chevy Chase Street, Jamaica, NY 11432 USA, Tel - 718-454-3920, Fax - 718-454-6330, e-mail - PeressJ@nyc.rr.com.

## Gasoline (RVP 9)
Table 1
TANK EMISSION CALCULATION FORM1
( Note - Cells in pink are input cells. All other cells are calculated cells. )
DIRECTIONS: |  | Fill in pink input cells with specific tank description, dimensions, throughput and paint absorptance factor. For paint absorptance factor included in Table 1a below.
Tank No. |  | T-501 |  | Tank type | Vertical fixed roof |  |  | Date |  | 2026-07-29 19:12
Material stored |  | Gasoline (RVP 9) |  | Company |  |  |  | Performed by |  | Jimmy Peress
City |  | Newark |  | State | NJ
Description |  | Outdoor storage tank
|  | INPUT DATA | [5 empty] | CALCULATIONS
|  |  | Symbol |  | Units |  |  |  | Symbol |  | Units
Breathing losses
Molecular Weight | [6 empty] | Tank vapor space volume |  | Vv | 6217.75 | ft3
| Molecular weight |  | Mv | 67 | Lb/lb-mole |  | Vapor density |  | Wv | 0.058488 | lb/ft3
Tank design data | [6 empty] | Vapor space expansion factor |  | KE | 0.23798
| Shell height |  | Hs | 40 |  |  | Vented vapor saturation factor |  | Ks | 0.16286 | ft2
| Diameter |  | D | 20 | ft
| Liquid height |  | Hl | 40 | ft | Breathing losses |  |  | LB | 5144.5036 | lb/yr
| Avg. Liquid height |  | Hl | 20 | ft
| vapor space outage |  | Hvo | 20.2083 | ft | Working losses |  |  | Lw | 7348.3738 | lb/yr
| Tank volume |  |  | 94002.9552 | gallons
| Turnovers |  | N | 10 |  | TOTAL LOSSES |  |  | LT | 12492.8774 | lb/yr
| Net throughput |  | Q | 940032.91 | gallons/yr
| Tunover factor |  | KN | 1
| Working loss product factor |  | Kp | 1
Meteorological data | [7 empty] | Table 1a
| Daily ave. ambient temp. |  | TAA | 54.7458 | °F |  |  | Tank Paint Solar Absorptance
| Daily max. ambient temp. |  | TAX | 63.3833 | °F
| Daily min. ambient temp. |  | TAN | 46.1083 | °F |  |  | Tank Paint | Solar Absorptance
| Daily ambient temp. range |  | DTA | 17.275 | °F
| Tank paint solar absorptance (see adjacent table) |  | a | 0.68 |  |  |  | white/white |  | 0.17
| Daily total insolation factor |  | I | 1235.5816 | Btu/ft2-day |  |  | Aluminum/Specular |  | 0.39
[8 empty] | gray/light |  | 0.54
| Liquid bulk temperature |  | TB | 57.8258 | °F |  |  | Aluminum/Diffuse |  | 0.6
| Daily vapor temp. range |  | DTv | 35.9635 | °F |  |  | grey/medium |  | 0.68
| Daily ave. liquid surface temp. |  | TLA | 63.1081 | °F
| Daily max. liquid surface temp. |  | TLX | 72.099 | °F
| Daily min. liquid surface temp. |  | TlN | 54.1173 | °F
| VP @ daily ave. liquid surf. temp. |  | PvA | 253.4178 | mm Hg
| VP @ daily max. liquid surf. temp. |  | PvX | 300.9437 | mm Hg
| VP @ daily min. liquid surf. temp. |  | PvN | 212.1132 | mm Hg
| Daily vapor pressure range |  | DPv | 88.8304 | mm Hg
| Breather vent pressure setting range |  | DPB | 0.06 | psia
| Breather vent pressure setting range |  | DPB | 3.1029 | mm Hg
1Calculations performed on this spreadsheet are taken from the USEPA AP-42- Section 7.1 Organic Liquid Storage Tanks - January 1996. This spreadsheet is derived from materials provided by Jimmy Peress, PE, Tritech Consulting Engineers, 85-93 Chevy Chase Street, Jamaica, NY 11432 USA, Tel - 718-454-3920, Fax - 718-454-6330, e-mail - PeressJ@nyc.rr.com.

## Gasoline (RVP 13)
Table 1
TANK EMISSION CALCULATION FORM1
( Note - Cells in pink are input cells. All other cells are calculated cells. )
DIRECTIONS: |  | Fill in pink input cells with specific tank description, dimensions, throughput and paint absorptance factor. For paint absorptance factor included in Table 1a below.
Tank No. |  | T-501 |  | Tank type | Vertical fixed roof |  |  | Date |  | 2026-07-29 19:12
Material stored |  | Gasoline (RVP 13) |  | Company |  |  |  | Performed by |  | Jimmy Peress
City |  | Newark |  | State | NJ
Description |  | Outdoor storage tank
|  | INPUT DATA | [5 empty] | CALCULATIONS
|  |  | Symbol |  | Units |  |  |  | Symbol |  | Units
Breathing losses
Molecular Weight | [6 empty] | Tank vapor space volume |  | Vv | 195.3273 | ft3
| Molecular weight |  | Mv | 62 | Lb/lb-mole |  | Vapor density |  | Wv | 0.081288 | lb/ft3
Tank design data | [6 empty] | Vapor space expansion factor |  | KE | 0.39416
| Shell height |  | Hs | 20 |  |  | Vented vapor saturation factor |  | Ks | 0.2049 | ft2
| Diameter |  | D | 5 | ft
| Liquid height |  | Hl | 20 | ft | Breathing losses |  |  | LB | 468.0634 | lb/yr
| Avg. Liquid height |  | Hl | 10 | ft
| vapor space outage |  | Hvo | 10.0521 | ft | Working losses |  |  | Lw | 217.2893 | lb/yr
| Tank volume |  |  | 2937.5923 | gallons
| Turnovers |  | N | 6.8083 |  | TOTAL LOSSES |  |  | LT | 685.3527 | lb/yr
| Net throughput |  | Q | 20000 | gallons/yr
| Tunover factor |  | KN | 1
| Working loss product factor |  | Kp | 1
Meteorological data | [7 empty] | Table 1a
| Daily ave. ambient temp. |  | TAA | 54.7458 | °F |  |  | Tank Paint Solar Absorptance
| Daily max. ambient temp. |  | TAX | 63.3833 | °F
| Daily min. ambient temp. |  | TAN | 46.1083 | °F |  |  | Tank Paint | Solar Absorptance
| Daily ambient temp. range |  | DTA | 17.275 | °F
| Tank paint solar absorptance (see adjacent table) |  | a | 0.68 |  |  |  | white/white |  | 0.17
| Daily total insolation factor |  | I | 1235.5816 | Btu/ft2-day |  |  | Aluminum/Specular |  | 0.39
[8 empty] | gray/light |  | 0.54
| Liquid bulk temperature |  | TB | 57.8258 | °F |  |  | Aluminum/Diffuse |  | 0.6
| Daily vapor temp. range |  | DTv | 35.9635 | °F |  |  | grey/medium |  | 0.68
| Daily ave. liquid surface temp. |  | TLA | 63.1081 | °F
| Daily max. liquid surface temp. |  | TLX | 72.099 | °F
| Daily min. liquid surface temp. |  | TlN | 54.1173 | °F
| VP @ daily ave. liquid surf. temp. |  | PvA | 380.6102 | mm Hg
| VP @ daily max. liquid surf. temp. |  | PvX | 448.0463 | mm Hg
| VP @ daily min. liquid surf. temp. |  | PvN | 321.4848 | mm Hg
| Daily vapor pressure range |  | DPv | 126.5615 | mm Hg
| Breather vent pressure setting range |  | DPB | 0.06 | psia
| Breather vent pressure setting range |  | DPB | 3.1029 | mm Hg
1Calculations performed on this spreadsheet are taken from the USEPA AP-42- Section 7.1 Organic Liquid Storage Tanks - January 1996. This spreadsheet is derived from materials provided by Jimmy Peress, PE, Tritech Consulting Engineers, 85-93 Chevy Chase Street, Jamaica, NY 11432 USA, Tel - 718-454-3920, Fax - 718-454-6330, e-mail - PeressJ@nyc.rr.com.