## Slide 1
Stanley V. Cach Jr., P.E., P.P., BCEE., D.WRE
NJDEP Project Manager
Division of Water Quality
Wet Weather Flow Treatment and Disinfection Demonstration Project
“A Cost-Effective 21st Century Solution to a
20th Century Problem”
NJ Clean Water Council
November. 14, 2017

## Slide 2: The Report
Background
Project Objectives
Project Collaboration
Technologies Tested
Findings
Conclusions
October 2017

## Slide 3: Background: CSO Options
ELIMINATE REDUCE/STORE TREAT
Separate Green POTW
I/I Reduction Gray Satellite/End of Pipe
LID
S/F Removed 700 Tons/YR
281
Individual CSO Outfalls
Permitted
71
CSO Outfalls
Eliminated
210 CSO Outfalls
CSO FLOW
~23 BGY

## Slide 4: Background: A Cost Effective Alternative
Satellite/End of Pipe Technologies
  CSO Feasibility Studies (2005-2007)
    Technologies were limited & not fully proven
    Performance was not independently validated
  SSO Abatement Alternative Analysis (2014)
    Satellite technologies chosen instead to storage, transport and treat at POTW

## Slide 5: One Comprehensive Study: Wet Weather Flow Treatment & Disinfection Demonstration Project
One study for all CSO permittees
Purpose: verify performance & costs
Duration: over 2 years (2014-2015)
Location: Oak Street Facility, City of Bayonne
Collaboration:
  Technical Advisory Committee
  Regulatory Oversight Team

## Slide 6
Project Collaboration
Project Leadership
NJDEP
Division of Water Quality
Bayonne Municipal Utilities Authority
Mott MacDonald (Project Manager)
Regulatory Oversight Team (15)
NJDEP
Division of Water Quality
Division of Water Monitoring & Standards
Office of Quality Assurance
Office of Science
USEPA
Office of Research and Development – Edison
Quality Assurance Staff
Rutgers University
Technical Advisory Committee (7)
NJDEP
Division of Water Quality
USEPA
Office of Research and Development – Cincinnati/ Edison
Rutgers University
Mott MacDonald
Moffa and Associates Consulting Engineers
Operational Support
Passaic Valley Sewerage Commission
Suez/ United Water
Notes: Who: A collaborative funding & technical effort
  City of Bayonne; NJDEP; USEPA; Rutgers University; PVSC & Technology Manufacturers.
  Collaboration & peer review
    Technical Advisory Committee & Regulatory Oversight Committee.

## Slide 7
Project Collaboration:
Technical Advisory Committee
Committee Members:
Peter Moffa, P.E.
Richard Field P.E., D.WRE, BCEE (EPA ORD, Retired)
Jurek Patoczka, PhD, P.E.
Daniel Murray, P.E. (EPA ORD)
The Trinity
Committee Members (cont’d):
Qizhong Guo, PhD, P.E. (Rutgers)
Stanley Cach, P.E., D. WRE BCEE (NJDEP)
Shadab Ahmad, P.E. (NJDEP)

## Slide 8: Demonstration Project Site
Bayonne
MUA
Project Site
Newark Bay
Kill van Kull

## Slide 9: Project Objectives
Select & verify the performance of end of pipe technologies to treat CSO discharges
  Under field conditions
  For solids removal & disinfection
  At remote satellite locations
Improve engineering practitioners understanding of wet weather technologies
  Reliability
  Scalability
  Anticipated capital and O & M costs

## Slide 10: Technologies Tested: SIX (6) PILOT TECHNOLOGIES
Technology | Type | Function
Storm King | Vortex | Solid removal
Terre Kleen | Plate settler unit | Solid removal
Flex Filter | Compressed media filter | Enhanced solid removal
Trojan | Low pressure UV | Disinfection
Aquionics | Medium pressure UV | Disinfection
Injexx/Verdent | Peracetic acid (PAA) | Disinfection
18 treatment scenarios during 9 storm events
200-300 samples per event
Notes: Flex Filter
Compressed media filter
Advanced solid removal

## Slide 11: Why These Technologies?
Technologies were chosen for their:
  Suitability for remote satellite facilities
  Documented performance
    Ability to meet CSO performance limits
  Simple operation
  Small footprint
  Ease of maintenance
  Cost
    Construction and O&M
Flex Filter
Storm King

## Slide 12: Why High-rate Solids Removal?
Vortex type- Storm King
  A vortex hydrodynamic solids separation w/ swirl self-cleaning screen
  No moving parts & non powered
  Remote & self-activating
  Anticipated reduction:
    TSS: 30-50%
    BOD: 20-30%
Plate Settler Unit- Terre Kleen
  Gravimetric solids separation
Terre Kleen

## Slide 13: Why Enhanced High-rate Solid Removal?
Compressed Media Filter – FlexFilter
  Innovative technology
  Remote, simple operation
  No chemicals required
    No ramp up time
  Anticipated reduction:
    TSS: 85-90%
    BOD: 50-60%
  Self contained & easy retrofit
Flex Filter

## Slide 14: Why Chemical Disinfection?
Peracetic Acid - Injexx/Verdent
  Emerging technology per USEPA
  High rate disinfectant
    Stronger oxidant than hypochlorite
    No harmful by-products
    Could require no neutralizing agents
    Longer effective shelf life
    Contact time less than 5 minutes
  Can be used in combination w/ UV
Injexx/Verdent

## Slide 15
Demo Project Site (Aerial View)
Disinfection
Solid Removal
Influent

## Slide 16
WWETCO
Bio-FlexFilter™
(Compressed Media Filter)
Backwash Ends
Filter Drain
Media Compression
Filtration
Backwash
Video courtesy of WesTech
Video

## Slide 17
Photos Courtesy of
WesTech Engineering, Inc.

## Slide 18: Technology Findings
Flex Filter (Enhanced High-rate Solid Removal)
  Effectively reduces TSS (90%) for UV or chemical disinfection treatment
  Flex Filter effluent concentrations for TSS & CBOD averaged 25 & 48 mg/l respectively (excluding the first event)
Flex Filter
Storm King
Storm King & Terre Kleen (High-rate Solid Removal)
  Effective treatment for grit removal/inorganics
  Unable to reduce lighter solids for UV disinfection treatment

## Slide 19
Trojan & Aquionics (UV)
  The Trojan UV 3000Plus unit using low-pressure-lamps:
    Required approx. 25 mJ/cm2 irradiation energy input
    Achieved 3 log (ave.) inactivation of pathogen indicators
  The Aquionics 250+W unit using medium-pressure lamps:
    Required more than 45 mJ/cm2 irradiation energy input
    Achieved a 3 log (ave.) inactivation of pathogen indicators
Trojan
Technology Findings (cont’d)
Notes: Define water quality objectives

## Slide 20
Trojan & Aquionics (UV)
  As expected, there was a strong correlation between water transmittance and water quality parameters concentrations for TSS, CBOD5 & COD
  As these parameters’ concentration increased, UVT decreased
Aquionics
Technology Findings (cont’d)
Notes: Define water quality objectives

## Slide 21
5. Injexx/Verdent (Peracetic Acid – PAA at 12% solution)
  Positive correlation between the applied dose of PAA as normalized by COD present in the wastewater and the log reduction of pathogen indicators
  PAA dose of 0.01 mg/l of PAA per mg/l of COD present in wastewater resulted in 3 log reduction of fecal coliforms (on average) with slightly higher effectiveness for E. coli and slightly lower for Enterocci
Technology Findings (cont’d)
Injexx/Verdent
  Increasing the relative dose to above 0.015 mg/l of PAA per mg/l of COD increased log reduction to 4 (limited data)
  Hydraulic retention time ~ 3 minutes
Notes: Define water quality objectives

## Slide 22: Technology Conclusions
Coarse screens (1/2” opening) should precede any treatment scenarios
Compressed media filter – Flex Filter
  Most consistent and effective solids-removal technology
UV
  Effectively achieve water quality objectives at 40% UV transmissivity or greater
  Compressed media filtration, or equivalent, must precede UV
  The effluent from the Flex Filter averaged approx. 27 mg/l for TSS & 40% on UVT (excluding simulation runs)

## Slide 23: Technology Conclusions(cont’d)
Peracetic Acid
  Effective disinfectant for wet weather flows
  Compared to chlorine:
    Similar or lower dosages needed
    Shorter contact time required (typ. 3 mins.)
    No neutralizing agent required
    Potentially less toxic then chlorine
    Longer shelf life
Flex Filter - Compressed media filter, followed by UV and/or Peracetic acid disinfection, can achieve water quality standards (suspended solids and disinfection)

## Slide 24: Costs Conclusions
Construction and Operation & Maintenance (O&M) Costs
  can be significantly lower than regional solutions (transport and treatment or sewer separation)
Equipment and O&M cost curves are available in section 12 of the report
Estimated Footprint, Construction and O&M Costs:
Compressed Media Filter
Design Flow (MGD) | Filter Matrix Cell (width x length)1 | Matrix Foot Print2 Square Feet -Acres |  | Construction Cost 3 ($M) | Annual O/M Cost4 ($)
5 | 5(6x12) | 1,700 | 0.04 | 3.1 | 17,200
10 | 5(6x24) | 2,200 | 0.05 | 4.0 | 23,400
25 | 5(13x30) | 5,400 | 0.11 | 9.8 | 36,600
100 | 10(27x30) | 21,000 | 0.48 | 38.0 | 104,800
250 | 24(27x30) | 50,000 | 1.15 | 90.5 | 226,000

## Slide 25: Project Conclusions
High-performance satellite end-of-pipe treatment can:
  be used to protect public health and aquatic biology
  be a cost effective alternative
  provide incremental CSO reductions
  offer green spaces & other community amenities
Satellite Treatment
facilities can be:
  Unmanned
  Odor free
  Adaptable to multiple
  locations
    Small footprint
    Below grade

## Slide 26: Springfield, Ohio – WTP:
Courtesy of Black & Veatch
CMAS
Auxiliary EHRT Facility
High-rate/ High-performance CSO treatment
Compressed media filter and chemical disinfection technologies
Operating Power: < $5 per MGD for CSO treatment
Small footprint

## Slide 29: Access the Full Report
nj.gov/dep/dwq/cso-wet.htm

## Slide 30: Wet Weather Flow Treatment & Disinfection Demonstration Project
nj.gov/dep/dwq/cso-wet.htm
Stanley V. Cach Jr., P.E., P.P., BCEE., D.WRE
NJDEP Project Manager
Division of Water Quality
John Dening, CFM, P.E.
Mott MacDonald
Senior Project Manager
&