Sand Filter with Underdrain

Basin #___ on the Location Map

Development Name: ___________________________

Township, County: ___________________________

Location of Basin: X: ______; Y: ______ (or N: ______; E :_____)

Location Description: e.g., Northwest corner of the development, near County RT 531

Location Map

N E County Route 531 Discharge Grass Swale #1 Basin #1 Drywell #1 Corporation Road Building Parking Lot Vegetative Filter strip #1 Drywell #2 Access Grass Swale #2

Example Map: Use aerial photo, site plan, or other graphics showing the locations of BMPs.

NOTE

This Field Manual is intended to be editable and adjustable in accordance with the design of stormwater management measures, the site conditions, and the special needs of responsible party. The Engineer should supplement information and best management practice to assist the responsible party to perform maintenance.

Blue text indicates information may be deleted and or replaced as necessary.

Table of Contents

Sand Filter with Underdrain Overview	4

Basic Design Information	5

Visual Aid for Dry Type Stormwater Basin Inspection	8

Reference Documents	13

Inspection Checklist / Maintenance Actions	15

Preventative Maintenance Record	23

Corrective Maintenance Record	24

# Sand Filter with Underdrain Overview

Functionality

Sand filters with underdrains are stormwater management systems designed to maximize the removal of pollutants from stormwater.  They consist of a pre-treatment zone and a treatment zone.  The treatment zone includes a sand bed and underlying components.  Pollutants are treated through settling, filtration, and adsorption by the sand bed.

Proper care and attention in the long-term maintenance of the stormwater management measure is critically important to the safety and health of the public.

Type of BMP – Dry Basin / Filtration Only

A sand filter with an underdrain is a type of dry basin.  Dry basins must fully drain within 72 hours of the most recent rainfall.  Standing water in excess of 72 hours is a sign of basin failure.  Standing water in excess of 72 hours is a sign of basin failure. It may also contribute to mosquito breeding and other health and safety issues.  The design drain time shall be closely monitored to ensure that potential failure is recognized early.  This sand filter is designed with an underdrain piping system.  Therefore, runoff leaves the system via infiltration into the underlying perforated pipes.

A sand filter with an underdrain can also be designed for extended detention, in which case it will attenuate peak flows from storms larger than the Water Quality Design Storm.

For the field manual for a sand filter with infiltration, please see: Sand Filter with Infiltration Field Manual.

# Basic Design Information

This section shall be filled out by the design engineer.

Hydrology Design Targets

- This sand filter is designed with a sand bed permeability rate of _________ inches/hour (pre-construction) and __________ inches/hour (post-construction - tested on   (MM)  /  (DD)  /  (YYYY)  ).

- The design drain time is __________ hours.

- The elevation of the seasonal high water table of this basin was observed on

(MM)  /  (DD)  /  (YYYY)   and it was _________ feet below the basin bottom surface, at EL._______ feet.

- This basin will be discharged to (municipal stormwater sewer system/ combined sewer system/ stream (stream name).)

Hydraulic Design Targets

- Design parameters

|  | Water Quality Design Storm | 2-year storm | 10-year storm | 100-year storm |
| --- | --- | --- | --- | --- |
| Rainfall Depth (inches) | 1.25 inch in 2 hours | ___ inches in 24 hours | ___ inches In 24 hours | ___ inches In 24 hours |
| Runoff Volume (cubic feet) |  |  |  |  |
| Peak Flow Rate (cfs) |  |  |  |  |
| Water Surface Elevation (feet) |  |  |  |  |

Note: The design engineer shall fill out the table in accordance with the design of the stormwater management measure. If the item is not applicable, enter N/A in the table.

- The emergency spillway is at EL. ___________ feet (if applicable).

Basin Configuration Targets

- Pretreatment is provided by (BMP Type: __________, BMP No.). A perforated riser (is / is not) used.

- Outlet Information:

| Outlet Description | Outlet Type | Orifice Size / Weir Length | Invert Elevation |
| --- | --- | --- | --- |
| Water Quality Orifice |  |  |  |
| Outlet #1 |  |  |  |
| Outlet #2 |  |  |  |
| (Other) |  |  |  |

- Sand Layer

  - The depth of sand layer shall be ______ inches, which requires a volume of ________ cubic feet of sand.

  - The invert elevation of the sand layer is EL. ________ feet.

  - The sand layer is designed to be replaced every __________ months.

  - The sand bed (is / is not) covered by top soil and vegetation.

- Top soil (if applicable)

  - The permeability rate of the top soil must be at least twice the design permeability rate of the subsoil. The top soil permeability rate is _________ inches/hour (pre-construction) and __________ inches/hour (post-construction - tested on

(MM)  /  (DD)  /  (YYYY)  ).

- Underdrain

  - The perforated laterals are ________ inches in diameter, at a slope of ______%.

  - There are _____ lateral pipes in the basin. Each lateral is ______ feet long.

  - The perforations are _____ inches in diameter and are arranged _____ inches center to center, ______ perforations per row, and _______ rows of perforations per pipe.

  - The manifold pipe is ______ inches in diameter, (perforated / not perforated), at a slope of _________%, and _______ feet in length.

(Note: The cleanout pipe shall not be perforated.)

  - Filter fabric is installed to wrap around the laterals. The material used for the filter fabric is _____________, and has a permeability rate of _________ inches per hour.

  - The gravel layer surrounding the underdrain consists of _______ inches of gravel above the underdrain and _______ inches of gravel below the underdrain.

- Vegetation

  - The top of the sand bed is designed to (have / have no) vegetation.

Note: The only type of vegetation allowed on a sand filter is turf grass.

Critical Maintenance Features

- No heavy equipment on the basin surface or sand layer.

- Keep the sand layer surface clean and no accumulation of dead leaves.

- Ensure no standing water in the drainage pipe and outlet structure.

- Grass clippings shall be collected from the basin and properly disposed.

- (Others to be added by the design engineer, if necessary)

Attach the following Disturbance Notices, if applicable to the site:

Wetland Disturbance Notice:

Maintenance of this BMP may disturb a wetland area. Contact NJDEP Division of Land Use Regulation for guidance and any required permit(s) before performing maintenance.

Wildlife Disturbance Notice:

Maintenance of this BMP may disturb or remove vegetation in an area designated to endangered and/or threatened species. Contact NJDEP Division of Fishing and Wildlife for guidance and any required permit(s) before performing maintenance.

# Visual Aid for Dry Type Stormwater Basin Inspection

(Note: Basins shown here include various types of dry basins, not limited to the category of basin in this field manual.)

| Courtesy of NJDOT |  |  |
| --- | --- | --- |
| Issue: Corrective Action: Preventative Action: |  | The inlet is not properly drained, assuming it has not rained within 72 hours. Clear and remove sediment. Check whether the water table is at or above the bottom of the forebay. Also check the permeability of the underlying soil, if necessary. Routine inspections and removal of sediment from the forebay. |
| Courtesy of NJDOT |  |  |
| Issue: Corrective Action: Preventative Action: |  | The Inflow pipe is clogged by sediment and vegetation. Clear and remove sediment and unwanted vegetation. Routine inspection and removal of sediment and unwanted vegetation. |
| Courtesy of NJDOT |  |  |
| Issue: Corrective Action: Preventative Action: |  | The Inflow pipe is entirely clogged by sediment and trees. Clear and remove sediment and trees. Routine inspection & removal of sediment and unwanted vegetation. |
| Courtesy of NJDOT |  |  |
| Issue: Corrective Action: Preventative Action: |  | The excessive sediment in inflow pipe (shown above) might be caused by a blockage of flow to the basin due to excessive vegetation and overgrown trees. Clear and remove trees and vegetation. If necessary, re-grade the bottom slope to ensure the flow properly spreads over the basin bottom. Routine inspection and removal of sediment and unwanted vegetation. |
| Courtesy of NJDOT |  |  |
| Issue: Corrective Action: Preventative Action: | Eroded inflow apron. Repair apron. Routine inspection and rehabilitation, if necessary. |  |
| Courtesy of NJDOT |  |  |
| Issue: Corrective Action: Preventative Action: | The vegetation loss and the blackish soil may indicate frequent inundation. Check the permeability rate of the soil and the water table elevation. Replace the soil if necessary. Routine inspection and tilling/aeration, if necessary. |  |
| Issue: Corrective Action: Preventative Action: | The low flow channel has excessive accumulation of sediment and debris. The outflow orifice is clogged by a trash bag and debris. Note that there is no trash rack installed. Check the permeability rate of the soil and the water table elevation. Replace the soil if necessary. Routine inspection and cleaning. |  |
| Courtesy of NJDOT |  |  |
| Issue: Corrective Action: Preventative Action: | Trash rack is damaged. Repair the trash rack. Routine inspection, especially after large storm events. Tighten any loose bolts and repair structural flaws. |  |
| A well maintained detention basin |  |  |

# Reference Documents

Documents to be placed in this field manual should include the following:

- As-built Drawings with Drainage Plans

- Soil Boring Logs

- Permeability Test – Sand Layer

- Filter Fabric Information

- Underdrain Pipe Specifications

- Groundwater Mounding Analysis

Attach Reference Documents Here

# Inspection Checklist / Maintenance Actions

Sand Filter with Underdrain

Checklist (circle one): Quarterly / Annual / Monthly / Special Event Inspection

Checklist No. ______________    	Inspection Date: _______________

Date of most recent rain event: __________

Rain Condition (circle one):

Drizzle / Shower / Downpour / Other _____________

Ground Condition (circle one):

Dry / Moist / Ponding / Submerged / Snow accumulation

The inspection items and preventative/corrective maintenance actions listed below represent general requirements. The design engineer and/or responsible party shall adjust the items and actions to better meet the conditions of the site, the specific design targets, and the requirements of regulatory authorities.

|  | For Inspector |  |  | For Maintenance Crew |
| --- | --- | --- | --- | --- |
| Component No. Component Name | Inspection Item and Inspection Item No. |  | Result | Preventative / Corrective Maintenance Actions |
| A1 Pretreatment (Forebay) | 1 | Scouring or erosion is present at inlet structure and/or riprap apron | Y__ N__ | Check the flow diversion device before the inlet pipe and whether the bypass flow channel is clogged Work Order # __________ |
|  | 2 | Clogged pipes or excessive sediment in the forebay | Y__ N__ | Remove sediment or debris |
|  | 3 | Damaged outlet structure (e.g., cracking, subsidence, spalling, erosion, or deterioration) | Y__ N__ | Repair or replace the outlet structure Work Order # __________ |
| A2 Pretreatment (MTD, If installed) | 1 | MTD inspection | Y__ N__ | (If a MTD is used for pretreatment, see manufacturer’s maintenance manual) |
| A3 Pretreatment (Structural BMP) | 1 | BMP inspection | Y__ N__ | (See BMP No. ________ Field Manual) |
| Note: |  |  |  |  |
| B1 Sand Bed | 1 | Standing water is present after the design drain time The observed drain time is approximately _________ hours. | Y__ N__ | Recheck to determine if there is standing water after 72 hours If standing water is present longer than 5 days, report to mosquito commission. |
|  |  |  |  | Remove any sediment buildup Replace the sand layer (volume of replacement sand is specified in the Basin Configuration Targets in the Basic Design Information Section of this Manual) Work Order # ______________ |
|  | 2 | Excessive sediment, silt, or trash accumulation on basin bed | Y__ N__ | Clean pretreatment system Remove silt, sediment, and trash |
|  | 3 | Erosion or channelization is present | Y__ N__ | Check whether the flow bypass or diversion device is clogged Re-grade the infiltration bed Work Order # ______________ |
|  | 4 | Animal burrows/rodents are present | Y__ N__ | Pest control Work Order # __________ |
|  | 5 | Uneven bed | Y__ N__ | Use light equipment to resurface the bed Work Order # _________ |
|  | 6 | Evidence of sinkholes or subsidence | Y__ N__ | Monitor for sinkhole development |
| Note: |  |  |  |  |
| B2 Underdrain | 1 | Standing water is present after the design drain time | Y__ N__ | Check whether the outlet is clogged Check whether the underdrain pipes are clogged or damaged Ventilate the underdrain pipes Work Order# _________ |
|  | 2 | Sand or pea gravel present in the discharge pipe or outfall of the sand filter | Y__ N__ | Check whether the filter fabric around the pipe is broken and repair if necessary Work Order# __________ |
|  | 3 | Continuous discharge of water from the outfall when it has not rained within the past 72 hours and the bed is completely dry | Y__ N__ | Check whether the seasonal high water table is above the bottom of the sand filter A retrofit may be required if the system is intercepting groundwater Work Order# __________ |
| Note: |  |  |  |  |
| C Vegetation | 1 | Large spot(s) showing bare soil | Y__ N__ | Vegetative cover must be maintained at 85%. Revegetate the entire basin if 50% or more vegetation has been lost Check Landscaping plan for guidance (if available) Work Order # __________ |
|  | 2 | Overgrown vegetation | Y__ N__ | Mow/trim the vegetation Work Order # _______ |
|  | 3 | Tree growth in the basin | Y__ N__ | Clear, trim, or prune the trees according to the original Vegetation or Landscaping Plan Inspect to determine if the tree roots caused any structural damage Work Order # __________ |
| Note: |  |  |  |  |
| D Basin Embankment and Side Slopes | 1 | Signs of erosion, soil slide or bulges, seeps and wet spots, loss of vegetation, or erosion on the basin slope | Y__ N__ | Check for excessive overland runoff flow through the embankment. Check for any sink hole development Direct the overland runoff to the forebay or pretreatment area Restabilize the bank Work Order # __________ |
| E Outlet | 1 | Trash or debris accumulation more than 20% | Y__ N__ | Clean and remove Determine source of trash and address to reduce future maintenance costs or basin failure |
|  | 2 | Trash rack is damaged or rusted greater than 50% Trash rack is bent, loose, or missing parts | Y__ N__ | Repair or replace trash rack Work Order #__________ |
|  | 3 | Outlet components (e.g., orifice plates or weir plate) skewed, misaligned, or missing | Y__ N__ | Repair or replace component Work Order #__________ |
|  | 4 | Discharge pipe apron is eroded or scoured | Y__ N__ | Restabilize the discharge riprap apron Work Order #__________ |
|  | 5 | Standing water is present in the outlet structure longer than 72 hours | Y__ N__ | Pump out the standing water Work Order # __________ |
| Note: |  |  |  |  |
| F Emergency Spillway | 1 | Trees or excessive vegetation present | Y__ N__ | Remove trees and roots, and restore berms if necessary Work Order #________ |
|  | 2 | Damaged structure | Y__ N__ | Repair Work Order #________ |
| G Miscellaneous (if applicable) | 1 | Fence: broken or eroded parts | Y__ N__ | Repair or replace Work Order #__________ |
|  | 2 | Gate: missing gate or lock | Y__ N__ | Repair or replace Work Order #__________ |
|  | 3 | Sign/plate: tiled, missing, or faded | Y__ N__ | Repair or replace Work Order #__________ |
|  | 4 | Excessive or overgrown vegetation blocking access to the basin | Y__ N__ | Clear, trim, or prune the vegetation to allow access for inspection and maintenance Work Order #________ |
| Note: |  |  |  |  |

Follow Up Items (Component No. / Inspection Item No.):

(e.g., B/1, C/2)

Associated Work Orders: # ______, # ______, # ______, # ______, # _____

________________________       ______________________    ________________

Inspector Name                             Signature                                Date

Report issues to the local authority and mosquito commission as required by local ordinances and regulatory authorities.

File this checklist in the Maintenance Log after performing maintenance.

# Preventative Maintenance Record

Corresponding Checklist No. ________

Component No._______, Inspection Item No.________

Work Logs

| Activities | Components | Date Completed |
| --- | --- | --- |
| Sediment/debris removal Sediment removal should take place when the basin is thoroughly dry. | A1/A2/A3 – Pretreatment |  |
|  | B1 – Sand Bed |  |
|  | D – Basin Embankment and Side Slopes |  |
|  | E – Outlet |  |
| Vegetation removal | A1/A2/A3 – Pretreatment |  |
|  | B1 – Sand Bed |  |
|  | D – Basin Embankment and Side Slopes |  |
|  | E – Outlet |  |
|  | F – Emergency Spillway |  |
| (List additional tasks, if applicable) |  |  |

Vegetation is removed by _____________ (type of equipment) with minimum disruption to the remaining vegetation.

All use of fertilizers, pesticides, mechanical treatments, and other means to ensure optimum vegetation health must not compromise the intended purpose of the stormwater management measure.  The fertilizer applied is ____________ (type), and _________ (quantity per usage) is applied _____________ (frequency of use).

Debris, sediment, and trash are handled (onsite / by ____________ (contractor name) to disposal site _________________). (See Part I: Maintenance Plan – Disposal Plan Section)

Replacement of the sand layer will occur according to the scheduled frequency (see Basin Configuration Targets above).  The next scheduled replacement is _____________ (date).

Crew member:___________________/_________________    Date: _____________

(name/ signature)

Supervisor:_____________________/__________________   Date: _____________

(name/ signature)

File this Preventative Maintenance Record in the Maintenance Log after performing maintenance.

# Corrective Maintenance Record

- Work Order # ______________________ Date Issued _____________

- Issue to be resolved:

(e.g., orifice plate is loose and bent)

- The issue was from Corresponding Checklist ________, Component No. (e.g., E-outlet), Inspection Item No.      (e.g., 2, 3)	.

- Required Actions

| Actions | Planned Date | Date Completed |
| --- | --- | --- |
| New bolts to fix the orifice plate |  |  |
| Repair/replace the trash rack |  |  |
| Restabilize side slope (indicate location) |  |  |
| Repair riprap apron with 100 cubic yards of aggregate |  |  |
| Revegetate |  |  |
| (List additional tasks, if applicable) |  |  |

- Responsible person(s):

_____________________________________________________________

- Special requirements

  - Time of the season or weather condition:_________________________

  - Tools/equipment:____________________________________________

  - Subcontractor (name or specific type):___________________________

Approved by ___________________/_______________ Date _____________

(name/signature)

Verification of completion by ____________/________ Date _____________

(name/signature)

File this Corrective Maintenance Record in the Maintenance Log after performing maintenance.